SECTION 262550 – Single Breaker Load Bank Docking Station

GENERAL

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Comply with NFPA 70.

GUARANTEE/WARRANTY

The equipment installed under this contract shall be left in proper working order.  Replace, without additional charge, new work or material which develops defects from ordinary use within one year.

New materials and equipment shall be guaranteed against defects in composition, design or workmanship.  Guarantee certificates shall be furnished.

PRODUCTS

Single Breaker Load Bank Docking Station

Manufacturers:  Subject to compliance with requirements, provide products by the following:

TRYSTAR: SBVS --- The Vanjen Group, sales@vanjen.net

GENERAL REQUIREMENTS

Unit shall be a single breaker load bank docking station.  Docking station shall include one set of temporary Loadbank Camloks.

Entire package must be listed to ETL or UL 1008 Standards.  UL listing of individual components is not acceptable.

Enclosures:

Pad mount, NEMA 3R rain-tight, aluminum enclosure.

Pad-lockable front door shall include a hinged access plate at the bottom for entry of cables from portable generator or portable load bank. NEMA 3R integrity shall be maintained with access plate open for cable entry.

Front, side, and bottom through a front access panel shall be accessible for maintenance.

Top, side, and bottom through a front access panel shall be accessible for permanent cabling.

Finishes:

Paint after fabrication. Powder coated Hammer Gray.

Phase, Neutral, and Ground Buses:

Material:  Silver-plated, Tin-plated or Hard-drawn copper, specified upon order.

Equipment Ground Bus:  bonded to box.

Isolated Ground Bus:  insulated from box.

Ground Bus:  25%, 50% or 100% of phase size.

Neutral Bus:  Neutral bus rated 100 percent of phase bus.

Round edges on bus.

Entire construction shall be Bussing.  Cabling between Camloks or sections shall not be acceptable.

Temporary Load Bank connectors shall be Camlok style mounted on gland plate.

An additional Set of Mechanical Lugs, accessible from the front of the docking station, shall also be required for temporary loadbank connection on pad mount units.

Camloks are required to have phase color identification paint at their mounting point to the docking station.  Camlok phase paint shall be as follows

A phase – Brown

B phase – Yellow

C phase – Purple or Orange

N Neutral – White

G Ground – Green

Generator Circuit Breaker:

Circuit Breaker shall be rated per the project drawings

Siemens Model shall be constructed as follows:

XXXAF/AT

XXkAIC at 480V

ETU 745 LSIG Trip Unit

Breaker Open Close Aux Contacts – 2a/2b

120VAC/125VDC Shunt Trip Module

Circuit Breaker to be Kirk Key Interlocked to Male Camlok flip door.

Circuit Breaker shall be easily removeable for servicing

Voltage & Phase shall be as shown on project one line drawing. Camloks shall be color coded as appropriate for the specified voltage.

Amperage rating shall be as shown on project one line drawing.

A Load Dump Circuit will be provided, so that if the Utility power were to fail during a temporary load bank test, the load bank would shed itself and allow the generator to pick up the building load.

EXECUTION

EXAMINATION

Examine elements and surfaces to receive Generator Docking Station for compliance with installation tolerances and other conditions affecting performance of the Work.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Surface, Flush or Base Mounted:  Specified with order.

Install anchor bolts to elevations required for proper attachment to Generator Docking Station.

Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

FIELD QUALITY CONTROL

Third Party Tests and Inspections to include the following:

Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

Perform the following infrared scan tests and inspections and prepare reports:

Initial Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each Generator Docking Station.  Remove front panels so joints and connections are accessible to portable scanner.

Generator Docking Station will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports, including a certified report that identifies Generator Docking Station and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

END OF SECTION 262550