GE Zenith Series DPB Distributed Power Busway

- SUMMARY

- This specification covers the electrical characteristics and general requirements for a continuous opening, low voltage horizontal distribution busway.

- System shall be designed primarily as an overhead distributed power distribution center. System shall be designed to be located near critical distribution points to power specific loads, servers and or work stations. Once installed, the completed system will provide a manageable, economical means for the distribution of power and communications. Distribution of power and communications will be made through the adaptation of tap off plug-in units mounted securely to the busway rails.

- Tap off points shall be easily modifiable for phase configuration and be safe for installation and decommissioning while the busway is in its live state. All tap off distribution points shall have safety features prohibiting their installation while under load.

- System shall be 100% recyclable and be shipped in recyclable containers and packing

- STANDARDS AND CERTIFICATION

  - The low voltage distribution busway shall be certified and manufactured to the follow standards:

- Underwriters Laboratories Standard, UL 857 – The common UL, CSA, and ANCE Standard for Busway that is derived from the fifth edition of CSA Standard C22.2 No. 27, the twelfth edition of UL 857, and the second edition of NMX-J-148-1998-ANCE.

- IEC 60439-2 Standard - Low-voltage switchgear and control gear assemblies - Part 2: Particular requirements for bus bar trunking systems (busways)

- IEC 60264 Standard – Use of the Busway housing assembly as the protective ground conductor.

- Low Voltage Directive (73/23/EEC) including Amendment (93/68/EEC).

- IEC 60364 Standard – Requiring that the tap-off units instantly connect loads or secondary runs

- IEC/EN 60439-2 Standard –IEC standard for busway systems with installation standards and regulations for busway with an additional internal conductor with a cross-section equal to half that of the phases.

- Low Voltage Switchgear and Control gear Assemblies, Part 1: Type Tested and partially type tested Assemblies, IEC 60439-1: 1999. Part 2: Particular Requirements for Bus Bar Trunking systems (Busways), IEC 60439-2: 2000

- Compliant for: CUL Listing

- Compliant for: National Electric Code (NEC)Article 364 – Busways 19

- Compliant: NEMA AB1, Molded Case Circuit Breakers and Molded Case Switches

- Compliant: NEMA KS-1, Enclosed and Miscellaneous Distribution Equipment Switches (600VAC).

- Compliant: NFPA 70 – National Fire Protection Agency

- SYSTEM DESCRIPTION

  - Electrical Requirements:

- Rated system voltage: 480V

- Operating Frequency: 50/60 Hz

- Ampacity Rating at Full Load: (160), (225), (250), (400), (600), (800)

- Ground Capacity: Minimum of 150% of Rating

- Neutral Capacity: Minimum of (100%), 150%) of Rating

- Short Circuit Rating shall be: (22KAIC, up to 480V; 42KAIC, up to 208V)

- Grounding: One piece aluminum housing assembly

- Conductors: Individual isolated and insulated

- Conductors: 3 Phase Bus, 1 Neutral Bus

- Conductors shall be nickel-plated copper

- Voltage Drop: Less than 1.8V per 100' of installed system

- Operating Temperature: 40°C / 104°F rise with no de-rating

- Position: 100% rating for any horizontal or vertical orientation.

  - Optional: Branch Circuit Monitoring

- The Branch Circuit Monitoring must be integrated into the busway delivering the measurement and management of the Bus and Tap Off loads to the customer’s building management system through   Modbus or SNMP protocols.

The Busway Monitor / Communications system shall be capable of monitoring and providing all power calculations for the total input power for each busway run. It is housed on the outside wall of the power input Box, and shall be able to monitor two independent sources for dual run applications.

The System output power parameters / calculations data shall include, but not be limited to:

- Voltage (L-L, L-N) for all three phases

- Overvoltage/Undervoltage Alarm Threshold

- Voltage THD

- Current – Phase, Ground, and Neutral

- Minimum & Maximum Current

- Demand and Percent Load Current

- Crest Factor

- Warning and Alarm Threshold

- kW,  kVA,  kVAR,  Power Factor, kWH

- The Busway Branch Circuit Monitoring System shall be capable of complete integration with GE’s current Branch Circuit Monitoring System (BCMS) Hub.

- Optional BCMS Hub System - this system integrates multiple BCMS devices, these devices can be end feed units or existing legacy equipment with BCMS installed.

- Modbus Protocol with optional SNMP interface

- Graphical representation of all devices including end feeds, tap off boxes, and existing legacy equipment with discrete addresses

- Standard time stamped reporting software with customization features to include exporting all points measured in Excel for owner manipulation.

- Open protocol/access to all features

- Embedded web server with IP addressable interface for remote monitoring

- Real time load management thru TCP/IP connection

  - Optional: Isolated Ground

- Optional isolated ground bus installed in the existing rail channel –  factory installed and tested.

- SUBMITTALS

- Submittals shall be in accordance with specified procedures. Submit shop drawing and product data for record and approval prior to shipment.

- All submittals shall include construction details; dimensions, weights, clearances, connection details and component layout. Include submittals for all tap off units including but not limited to breaker, communication, cabling and lengths as well as tap off unit schedules.

- All submittals shall include connection details for configurations, external wiring and connections, as well as the size and location of all conduit connections and terminations.

- Submittal shall include documentation regarding, transportation, handling and installation requirements.

- WARRANTY

  - The Busway manufacturer shall guarantee the entire system against defective material and workmanship for a period of one (1) year from installation date or eighteen (18) months date of shipment with optional extended warranty periods of two (2) and three (3) years.

- COMPONENTS

  - Housing Construction

- Housing shall be of a single piece extruded aluminum designed to act as a 100% ground conductor. Standard lengths must include 5, 6, 10, 12 foot. Bus bar conductor must not extend beyond the housing.

- Bus bar conductors must terminate a minimum of 1" (2.54cm) from the end of the housing assembly. The extruded housing must accommodated the direct insertion of hanger assemblies which attach directly to the housing assembly.

- Hanger assemblies shall include the option for ceiling mount, side wall mount, and must not interfere or obstruct the housing opening intended for the installation of tap off units.

- The complete assembly shall be of the continuous opening design, and shall have a slotted opening on one side of the bus to accommodate the insertion of the tap off units.

- All the bus systems shall be finger safe IP2X rated and tested.

  - Conductor and Conductor Assemblies

- All phase and neutral conductors shall be made of nickel-plated copper with a minimum of 98.9% electrical grade purity and sized to handle a minimum of 100% of the continuously rated current with ambient temperatures at or below 40°C/104°F. All conductors shall be electrically isolated from the housing using a Class 220 with 148°C. (300°F) fiber Glastic with non-propagating properties. All insulators must be UL recognized.

  - Conductive Fittings and Components

- All conductive fittings including Tees, Crosses, and Elbows etc. shall be of the same material from the same manufacturer. All insulating material shall be a class 220 148°C. (300°F) fiber Glastic non-propagating material. All insulators must be UL recognized.

  - Plug-in Tap Units

- Plug-in tap off units shall be polarity matched to the busway system.

- Plug-in tap off units shall use GE circuit breakers for branch circuit protection.

- Plug-in tap off units shall make Ground contact prior to full insertion in the bus system.

- Plug-in tap off units shall have a cam lock that requires all load breakers to be in the full OFF position prior to activation in the bus assembly

- Plug-in tap off units requiring a cord assembly shall be manufactured with cord grips and receptacles as specified in the drawings.

- All tap off boxes will be equipped to provide current/voltage  information for optional Branch Circuit Monitoring System and Branch Circuit Monitoring Hub devices.

- INSTALLATION

  - Busway

Runs will consist of specific factory manufactured straight lengths and fittings as shown on the approval drawings.

  - Suspension System

Using supplied mounting hardware the busway will be hung from the ceiling using threaded rod. Contractor shall be responsible for the connections on the supporting structure. Maximum hanger spacing will be no more than 10 foot on center – see installation manuals for recommendations for contractor. Height and plane changes of the busway system will be evaluated and submitted prior to release of final approval drawings.

  - Connecting Busway Sections

The installer will follow all manufacturers’ installation details. Specifications for the cam-operated splice joint will include the alignment of the position indicator on each joint in a straight line.

  - End of Runs

End pieces and end caps will be provided to install at the ends of each run.

  - Closure Components

The bottom opening of the bus system can be closed at any point along the system with the addition of the optional closure plate. Plates can be field modified for length and fit.