TYPE ZB3CT

COMBINATION AUTOMATIC TRANSFER

WITH BYPASS ISOLATION SWITCH

MX350 CONTROL

EFFECTIVE 11/30/2012

SUGGESTED SPECIFICATION

CLOSED TRANSITION

AUTOMATIC TRANSFER SWITCH

WITH BYPASS/ISOLATION OPERATION

WITH MX350 MICROPROCESSOR CONTROL

PART 1 - GENERAL

  - SCOPE

- Furnish and install Automatic Transfer Switches (ATS) with number of poles, amperage and voltage as shown on drawings. Withstand and Close-on ratings as listed in this specification are provided as a minimum requirement. Transfer Switches provided on this project without UL 3 cycle and 30 cycle ratings as detailed in this specification will not be reviewed or approved.

  - CODES and STANDARDS

The Automatic Transfer Switches and controls shall conform to the requirements of the

following:

Certification:

- UL 1008: Underwriters Laboratories Standard for Transfer Switch Equipment

- CSA C22.2 No. 178 @ 600 VAC or cUL: Automatic Transfer Switch

C.  Seismic Qualified to IBC-2009 & IEEE 693-2005

D.  OSHPD

Code:

- NFPA 70 National Electrical Code

- NFPA 99 Essential Electrical Systems for Healthcare Facilities

- NFPA 101 Life Safety Code

- NFPA 110 Standard for Emergency and Standby Power systems

- IEEE 241: Recommended Practice for Electric Power Systems in Commercial Buildings

- ANSI/IEEE 446: Recommended Practice for Emergency and Standby Power Systems

for Commercial Applications

- IEEE 602: Recommended Practice for Electric Systems in Healthcare Facilities

- NEMA ICS 10 CC1 (lug)

- NEC 517: Healthcare Facilities

- NEC 700: Emergency Systems

- NEC 701: Installation of Generators for Required Emergency and Standby Power

Supply System

- NEC 702: Optional Installation of Fuel Fired Generators for Emergency and Standby

Power Supply Systems for the One and Two Family Dwellings

- NEMA ICS 10 P1 Industrial Control and Systems Part 1: Electromechanical AC

Transfer Switch Equipment

- UL 508 Standard for Industrial Control

  - SUBMITTALS

A.  Manufacturer shall submit shop drawings for review, which shall include the following,       as a minimum:

1.  Descriptive Literature

2.  Plan, elevation, side and front view arrangement drawings, including overall              dimension, weights and clearances, as well as mounting or anchoring              requirements and conduit entrance locations.

3. Schematic diagrams

4. Wiring Diagrams

5.  Accessory list

PART 2 - PRODUCTS

2.01            ACEPTABLE MANUFACTURERS

- Automatic Transfer Switches and Bypass Isolation shall be General Electric Zenith Controls type ZB3CT. Any alternate must be submitted to the consulting engineer for approval at least 20 days prior to bid. Alternate bids must list any deviations from this specification.

2.02           CONSTRUCTION

A.    General

- The Closed Transition Automatic Transfer Switches and associated Bypass/Isolation Switch shall be furnished as shown on the drawings. Voltage and continuous current ratings shall be as shown.

- On 3-phase, 4 wire systems, utilizing ground fault protection, a true 4-pole switch shall be supplied with all four poles mounted on a common shaft. The neutral pole shall be designed to make first and break last. The continuous current rating and the closing and withstand rating of the fourth pole shall be identical to the rating of the main poles.

- The combination automatic transfer bypass/isolation switch shall be mounted in a NEMA 1 steel enclosure, unless otherwise indicated. The enclosure shall be sized to meet or exceed minimum wire bending space required by UL 1008.

- Both units shall be bussed together with silver plated copper bus to provide a complete pre-tested assembly. Construction shall be such that the contractor needs to install only power and control connections. All power and control connections shall be clearly identified for ease of installation.

- Bypass/isolation switches shall provide a safe and convenient means for manually bypassing and isolating the automatic transfer switch, with the ability to be used as an emergency back-up system in the event the transfer switch should fail. The bypass/isolation switch shall also have a mechanical interlock that will ensure that the same source contacts are closed, in parallel on both the stand-a-lone automatic transfer switch and bypass switch to prevent the alternate source from being inadvertently closed into a cross phase condition. In addition, the bypass/isolation switch shall be utilized to facilitate maintenance and repair of the automatic transfer switch.

- The automatic transfer switch shall be completely isolated from the bypass/isolation switch by means of an optional shutter system and separate access doors. The position and location of the ATS shall be mechanically and electrically annunciated during the isolating process.

- The combination automatic transfer and bypass switch shall be front, side and rear accessible

- The main contacts shall be capable of being replaced without removing the main power cable.

- All bolted bus connections shall have Belleville compression washers.

- When a solid neutral is required, a fully rated bus bar with required AL/CU neutral lugs shall be provided.

- Control components and wiring shall be front accessible. All control wires shall be multi-conductor 18 gauge 600 volt switchboard type in a point to point harness. All control wire terminations shall be identified with wire markers.

- The complete combination automatic transfer bypass/isolation switch assembly shall be factory tested to ensure proper operation and compliance with the specification requirements.

- Bypass Isolation Panel shall allow the user to successfully wind any over-center charge devices without un-intentional transfer of the contacts

- Bypass Isolation Panel contacts shall be operated only when prompted by the user

- The transfer switch shall be equipped with a safe external manual operator, designed to prevent injury to operating personnel.

- The transfer switch shall have the option of being equipped with a “Plug and Play” Interchangeable Source Cable Termination kit that enables installers to easily and quickly reconfigure the designation of Source 1 and Source 2 lugs.

- The transfer switch shall be eq	uipped with mechanical indicators that will enable operators to easily determine the automatic transfer switch’s racking position

B. Bypass/Isolation Construction

- All main contacts and operating linkages of the bypass/isolation section shall   be the same as the ATS, except that the operation of the bypass section shall be manual.

2. The manual bypass switch shall have the same electrical ratings as the                                               associated ATS. The main contacts of the bypass switch shall be mechanically

locked in either the normal bypass or the emergency bypass positions without the use of hooks, latches, magnets or springs and shall be silver-tungsten alloy, protected by arcing contacts. The switching mechanism shall provide “Quick-Make,” “Quick-Break” operation of the contacts.

- The primary buswork of the draw-out automatic transfer switch shall be               connected to the stationary bus stabs in the freestanding cubicle by silver             plated segmented, self aligning, primary disconnect fingers to facilitate proper    alignment between the removable draw-out when the ATS is withdrawn and       shall be available for inspection without disturbing or de-energizing the main      bus.

4.  The secondary control disconnect contacts mounted on the ATS shall be self-                                    aligning and shall plug into stationary elements mounted on the freestanding                                      cubicle.

- The racking mechanism of the bypass/isolation shall allow the ATS to be            disconnected from all sources of power and control without opening the              enclosure door. The transfer switch shall have a true draw-out configuration        that does not require disconnection of any electrical or mechanical device by       maintaining personnel. The automatic transfer and bypass/isolation switch shall have three modes of operation. Automatic: the ATS connected and in automatic operating mode; Test: the ATS is disconnected from the main bus but controls connected allowing testing of the ATS without impact on the load; Isolation: the ATS is completely disconnected from the bypass/isolation switch and free to be removed from the enclosure

6. A fourth pole, switched neutral shall be provided if the associated ATS is                    designed as a 4-pole. Basic 4-pole bypass/isolation switch construction shall be         identical to the associated ATS construction.

7.  Necessary controls shall be provided to ensure that the engine run circuit remains                             closed when the switch is in the bypassed to emergency position, even if the                                       associated ATS is in the normal position at Test mode or completely isolated

and the normal source is not available.

C. Automatic Transfer Switch

- The transfer switch shall be double throw, actuated by two electric operators momentarily energized.

- The normal and emergency contacts shall be positively interlocked mechanically and electrically to prevent simultaneous closing.  Main contacts shall be mechanically locked in both the normal and emergency positions without the use of hooks, latches, magnets, or springs, and shall be silver-tungsten alloy.  Separate arcing contacts with magnetic blowouts shall be provided on all transfer switches.

D.  Transfer Switch Controller

- The transfer switch shall be equipped with a Microprocessor Controller with a Power Supply Module, CPU and I/O Modules for all voltage and ampere ratings. The controller shall be capable of both Serial and Ethernet communications.

- The controller shall contain voltage sensing modules capable of direct single phase or three phase sensing of each source from 120 VAC to 600 VAC. The Power Supply Module shall accept a 120 VAC and 24 VDC external power source allowing controller communications in the event of a power outage.

- Voltage sensing shall be true RMS type and accurate to +/- 2% of nominal voltage. Frequency sensing shall be accurate to +/- 0.05Hz. The operating temperature range shall be –20 to +50 degrees C and storage from –40 to +90 C.

- The controller shall connect to the transfer switch through an interconnecting wiring harness. Interfacing relays shall be provided to isolate the controller from abnormal voltages applied to any and all customer input and output wiring terminals.

- All customer interface connections shall be wired to a common DIN rail Cage Clamp terminal block.

- The controller shall meet or exceed the requirements for Electromagnetic Compatibility as follows:

1. EN55022    (CISPR11) Conducted and Radiated emissions,

Class A

2. EN61000-4-2 (Level 4) ESD immunity test

ENG6100-4-3 (ENV50140) Radiated RF

EN61000-4-4 Electrical fast transient/burst immunity test

EN61000-4-5 IEEE C62.41 Surge immunity test

EN61000-4-6 (ENV50141) Conducted immunity test

EN61000-4-11 Voltage dips and interruption immunity

3. IEEE 472     (ANSI C37.90A) Ring wave immunity

E.   Controller Display and Keypad

1. A color, ¼ VGA minimum, graphical display shall be provided for viewing data

and setting operational parameters. Parameters shall also be available for viewing

remotely and limited control through a front accessible USB communications

port.

2. The Controller shall provide high intensity LED’s for the following:

a. Source Availability - Indicates the source voltage and frequency are within

preset parameters.

b. Source Connected - Indicates the source main contacts closed and the load

being served from the source.

c. XFER Inhibit - Indicates that the ATS is being inhibited from Automatic

operation to the unconnected source.

d. Alarm – Indicates an alarm condition is active.

e. TD Active – Indicates that a transfer switch time delay is actively timing.

3. For ease of navigation, the display shall include the following:

a. Soft Keys – Change function based on user location in the menu structure.

b. Dedicated Navigational Keys – Home, Scroll Up, End, Escape and Enter.

c. Dedicated Pushbuttons for Alarm Reset, Test, Control and Information.

Part 3 OPERATION

3.01 Voltage, Frequency and Phase Rotation Sensing

- Programmable voltage and frequency sensing of both sources capable of detecting single or three phase losses. The Controller shall have adjustable pickup and dropout settings for each source. Set point ranges as follows:

Parameter                     Sources                   Dropout/Trip               Pickup/Reset

Undervoltage                 N+E, 3phase              75 to 100%                     85 to 100%

Overvoltage                   N+E, 3phase              100 to 110%                   108 to 108%

Underfrequency             N+E, 3phase              45 to 59.8 HZ               45.1 to 59.5 HZ

Overfrequency               N+E, 3phase             50.1 to 63 HZ             50 to 62.9 HZ

- The controller shall monitor phase rotation of both sources and inhibit transfer if both sources are not the same phase rotation. (ABC or CBA)

- Settings shall be adjustable in 1% increments either through the keypad, USB port or     remotely via communications.

- A single source status screen shall be provided to allow for viewing of the status of both sources including three phase voltage, power and frequency.

3.02 Time Delays

A.  The controller shall include an adjustable time delay of 0 to 10 seconds to                                      momentarily override normal source power outages and to delay engine starting. The                    time delay shall be expandable up to 60 minutes if an external 120 VAC and 24 VDC                    power supply is provided for ATS control.

B. The controller shall include an adjustable 0 to 259 minute time delay on transfer to                  non-preferred, factory set at 3 seconds.

C.  The controller shall include a time delay on retransfer to the preferred source adjustable                   0 to 259 minutes, factory set at 30 minutes.

D. The controller shall include a time delay on engine cool down adjustable 0 to 60                    minutes, factory set at 5 minutes.

- The controller shall include a timer to control the transfer time from neutral to the           non-preferred source, adjustable 0 to 10 minutes, factory set at 5 seconds.

- The controller shall include a timer to control the time delay from neutral to the              preferred source, adjustable 1 to 10 minutes, factory set at 5 seconds.

- Closed Transition transfer switches shall include a Failure to Synchronize time delay      fixed at 60 seconds, for failure to synchronize Source 1 and Source 2 prior to closed       transition transfer.

- Closed Transition type transfer switches shall include a two-stage, back-up time delay system for protection against extended paralleling of both sources beyond 100 milliseconds. Should this time delay expire while in parallel, a contact will be provided to facilitate the tripping of an upstream circuit breaker to ensure extended parallel time does not exceed the local utility maximum time, typically 100 milliseconds.

I.   All time delays shall be adjustable in 1second increments. All time delays shall be

adjustable via the graphical display, the front USB port or configuration software

using the USB, serial or Ethernet communications port.

3.03 Additional Features

- Test Switch – The controller shall be provided with a two position, password

protected, test switch to simulate a normal source failure. The test mode shall be

configurable for Test without Load or Test With Load functionality. The Test function

shall be activated via the pushbutton on the display or remotely via a dry contact, voltage      signal or a network signal.

B.  Engine Start Signal – A SPDT contact, rated 10 amps at 28 VDC, shall be provided                           to start the engine generator in the event of a normal source outage.

C.  Source connected contacts rated 10 amps at 120 VAC shall be provided to signal

when the ATS is connected to each source.

D.  Source Connected LED’s – The controller shall include LED’s to indicate when the

ATS is connected to each source.

E.  Source Availability LED’s – The controller shall include LED’s to indicate the

availability of each source.

F.  Commit/No-Commit Transfer Selector – The controller shall include a

programmable selector to configure the controller to commit to transferring the

load to emergency (or not) in the event the normal source returns prior to the

generator being ready to accept load.

- Inhibit Transfer Signals – The controller shall be capable of accepting transfer

control inputs that inhibit transfer of the ATS to either source.

- Auto/Manual Selector – The controller shall include a programmable function to

select either Automatic or Manual operation.

- Auto/Manual Retransfer Selector Switch – The controller shall include a programmable function to retransfer from Source 2 to Source 1

- ATS/Engine Exerciser – The controller shall include a user configurable exerciser.

Exerciser shall be configurable for daily, 7 day, 14 day or 28 day exercise periods,                             each with (7) programmable events. The exerciser shall also be configurable as a

full, 365 day exerciser with up to 24 independent exercise events. Each event shall                            be configurable for Test with Load and Test without Load. Each event shall include                         user adjustable start time, date and test duration. All time and date settings shall be                            stored in non- volatile EEPROM memory. The controller shall include full                                         programmability for daylight savings time.

- Diagnostics – The controller shall contain self and system diagnostic screens for the purpose of detecting and troubleshooting abnormal system events.

L. Communications Interface – The controller shall be capable of interfacing via                                     serial/RS485 or optional Ethernet TCP/IP communications ports integral to the                                  controller. All communications parameters (baud rate, parity, IP Address, etc.) shall                          be accessible and programmable via the front keypad. Both serial and Ethernet                                  communication shall be Modbus open protocol.

M.  Event Logger – The controller shall have the ability to log data and to maintain the last

256 events, even in the event of a power failure. Time and date stamping of events

will be accurate to 1 ms. Controller shall be capable of synchronizing its date/time

setting with a main PC via Network Time Protocol over an Ethernet TCP/IP

network connection.

The following events shall be time and date stamped:

1.) Last Primary Source Failure

2.) Last reason for transfer.

3.) Last transfer to alternate source

4.) Last retransfer to primary source

5.) Time load is without power

6.) Time ATS powered up

7.) Total number of primary source failures

8.) Total number of transfers

N. Communications Modules

  - Serial Communications: Controller shall support RS485 communications             port to enable serial communications at baud rates up to and including                 115.2Kbps and be user configurable. The serial communications shall be             capable of a direct connect or multi-drop configured network.

  - Ethernet Communications: Controller shall be capable of supporting Ethernet     (Modbus TCP/IP) communications via an internally mounted and self-powered   communications card. Ethernet shall be 10/100 Mbit, auto sensing and include   a RJ45 network connector.

c.  Open Protocol: Both serial and Ethernet communications shall be Modbus                               protocol. Proprietary communications protocols shall not be acceptable.

O.  External Power Supply: The controller shall be capable of being connected to an                           external 120 VAC & 24 VDC power supply to permit full operation and

communications of the controller when both sources are de-energized.

- Auto Load Shed: The controller shall be capable of being programmed to               automatically shed the connected load in the event of a user configurable under      frequency condition.

- Customer Configurable Alarms – The controller shall be capable of being                configured to display customer configured alarm points. Alarms shall be capable   of being reset via a remote contact.

- Closed Transition transfer switches shall include the ability to select between open and closed transition operation either through the main controller or an optional keyed selector switch.

- Closed Transition transfer switches shall include a digital synchroscope for display of phase difference, in electrical degrees, between the two sources. Synchroscope data must be displayed in real time and accessible from the transfer switch main controller.

3.04 Power Quality Metering

- The ATS shall be able to supply optional metering for current, voltage, real power, reactive power, energy use, power factor and frequency. Metering shall be true RMS type, 1% accuracy for voltage and 0.5% for currents with a 5 amp secondary current transformer.

- The following parameters shall be provided:

1.) Phase current: Ia, Ib, Ic, In and average current (Iavg)

2.) Phase voltage: Va, Vb, Vc, Vab, Vac, Vbc

3.) Voltage and Current unbalance

4.) Hz, PF, W, Var, VA

5.) Wh, VARh

6.) Voltage and Current Harmonics (% THD up to 8th order)

7.) Phase Rotation Sensing

8.) Synchroscope (lead/lag)

C.  The ATS shall be capable of monitoring and capturing waveform data in the event        of a utility power outage or other user specified event.

- A total of 10 active channels of waveform capture may be user             configured.

- Each channel shall be capable of capturing up to 64 cycles of waveform information.

- Analog channels may be configured for 4, 8, 16 or 32 samples/cycle.

- Digital channels shall be configured for 1 sample/cycle.

- Waveform data shall be stored in industry standard COMTRADE format for broadest compatibility and ease of downloading to a PC.

D.   The controller shall be capable of logging digital and analog measured                                            parameters and storing the data in non-volatile memory.

- The controller shall contain a 10 channel Data Logger. Each channel    shall be capable of being configured to monitor a digital on/off or         analog measured parameter.

- The sampling rate of each channel shall be configurable form 1 cycle    to 60 minutes per sample. The data shall be stored in non-volatile memory in a first in, first out method.

PART 4 ADDITIONAL REQUIREMENTS

4.01 Withstand and Close Ratings

A. The ATS shall be UL listed in accordance with UL 1008 for 3 and 30 cycle close       and withstand ratings. ATSs that are not tested and labeled for 3 and 30 cycle,

ratings are not acceptable. The automatic transfer and bypass/isolation switch

shall be tested as a complete connected unit. Minimum UL listed close and

withstand ratings at 480 VAC shall be as follows:                                                                                                                                                Current                                           Size Amps           3 Cycle           30 Cycle           Limiting Fuses

1000-3000            100 Ka		85 Ka                200,000 Ka

B.   During 3 cycle and 30 cycle closing and withstand tests, there shall be no contact       welding or damage. The 3 cycle and 30 cycle test shall be performed without the        use of current limiting fuses. The tests shall verify that contact separation has not       occurred, and there is contact continuity across all phases. Test procedures shall         be done in accordance with UL-1008, and testing shall be certified by                         Underwriters Laboratories, Inc.

C.  When conducting temperature rise tests to UL-1008, the manufacturer shall                include post-endurance temperature rise tests to verify the ability of the ATS to          carry full rated current after completing the overload and endurance tests.

4.02 Manufacturer                                                                                                                                                                                                                                                                                                         A. The Transfer Switch manufacturer shall employ a nationwide factory, field                                    service organization, available on a 24 hours a day, 365 days a year call basis.                                                                                                                                                                                       B. The manufacturer shall include an 800-telephone number, for field service                                     contact, affixed to the inside of each enclosure.                                                                                                                                                                                                                                       C. The manufacturer shall maintain records of each transfer switch, by serial                                      number, for a minimum of 20 years.                                                                                                                                                                                                                                   4.03 Installation

A.  Automatic Transfer Switches shall be provided with adequate lifting means                                   for ease of installation of floor mounted enclosures.                                                                                                                                                                                                                               B.   Provide access and working space as indicated or required.